THERMAL SYSTEMS RETROFIT PROGRAM

Engineering Report / Draft for internal circulation only

Prepared by: Process Improvement Office

Revision: 0.7 beta     Date: 19 April 2026

For comments email retrofit-core@example.com

TABLE OF CONTENTS

A. Project Context	3

I. Site Conditions	3

1. Existing Boiler Room	3

a. Ventilation constraints	4

b. Access path	4

2. Temporary bypass plan	4

c. Isolation logic	4

B. Retrofit Scope	5

I. Mechanical scope	5

II. Controls scope	5

Appendix - Vendor Matrix	9

NOTE: page numbers above were typed manually after a rushed submission review.

A. Project Context

The retrofit program covers three production buildings, one auxiliary boiler room, and a legacy chilled-water loop that has been patched repeatedly over the last six years. Internal reviewers requested a document that can be sent to operations, finance, and maintenance without preparing three separate versions.

The retrofit program covers three production buildings, one auxiliary boiler room, and a legacy chilled-water loop that has been patched repeatedly over the last six years. Internal reviewers requested a document that can be sent to operations, finance, and maintenance without preparing three separate versions.

I. Site Conditions

The surveyed site contains mixed-age equipment, undocumented valve labels, and a maintenance access corridor that is routinely blocked by pallet storage during the night shift.

The surveyed site contains mixed-age equipment, undocumented valve labels, and a maintenance access corridor that is routinely blocked by pallet storage during the night shift.

1. Existing Boiler Room

Ceiling clearance varies from 2.18 m to 2.42 m. Instrument tubing runs diagonally across the north wall and interferes with the preferred crane path for exchanger replacement.

Ceiling clearance varies from 2.18 m to 2.42 m. Instrument tubing runs diagonally across the north wall and interferes with the preferred crane path for exchanger replacement.

a. Ventilation constraints

Current extraction fans are undersized for hot-weather commissioning. During summer test windows, air temperature near the mezzanine reached 41 C in the last maintenance log.

b. Access path

The temporary route for moving plate exchangers passes through a narrow service door, then turns around a cable tray support. This route is feasible only if spare drums are cleared in advance.

2. Temporary bypass plan

The bypass sequence must keep washdown circulation alive for both Building 2 and Building 3. Operators asked that no shutdown step begin before the sanitation window closes at 22:30.

c. Isolation logic

This subsection should clearly restart under Section 2, but the current draft inherited lettering from the previous subsection chain. Reviewers complained that the table of contents is therefore unreliable.

This subsection should clearly restart under Section 2, but the current draft inherited lettering from the previous subsection chain. Reviewers complained that the table of contents is therefore unreliable.

Observed Constraints Snapshot

| Area | Issue | Severity | Owner |
| --- | --- | --- | --- |
| Boiler Room | Low headroom near east pipe rack | High | Facilities |
| Roof plant | Valve tags missing or duplicated | Medium | Maintenance |
| Utility trench | Water ingress after heavy rain | High | Civil |
| Corridor C | Access blocked by packaging stock | Medium | Operations |

B.Retrofit Scope

The scope includes exchanger replacement, control panel cleanup, sensor label normalization, and operator handover documents. Budget approval is staged, so the report must preserve current section numbering for review cycles.

The scope includes exchanger replacement, control panel cleanup, sensor label normalization, and operator handover documents. Budget approval is staged, so the report must preserve current section numbering for review cycles.

I. Mechanical scope

Mechanical changes include two compact heat exchangers, one secondary pump skid, balancing valves, and rerouted branch drains for maintenance access.

II. Controls scope

Controls work includes point renaming, alarm rationalization, and one revised sequence to keep fallback circulation active during sensor disagreement.

Controls work includes point renaming, alarm rationalization, and one revised sequence to keep fallback circulation active during sensor disagreement.

Appendix - Vendor Matrix

Three shortlisted vendors submitted schedules in incompatible formats. The procurement team requested a single appendix so comments can be tied back to one version-controlled report.

Three shortlisted vendors submitted schedules in incompatible formats. The procurement team requested a single appendix so comments can be tied back to one version-controlled report.

End of draft. Some headings were manually formatted and are not connected to a real outline level.